GATEWAY

MODBUS RTU to MODBUS TCP

Installation procedure:

- Connect RS485 or RS232 line to device port

- Connect power supply – 9V DC, min 250mA

- Connect PC to Ethernet port and use Web Browser to set parameters

Default IP:	192.168.0.2

Default Port /both Modbus and HTTP/:	502

Factory reset procedure: press RESET button on first COMM led flash after power on

Holding Registers /Internal/

| Modbus Address | Description | Read/ Write |
| --- | --- | --- |
| 0 | Analog Input 0 | R |
| 1 | Analog Input 1 | R |
| 2 | Analog Input 2 | R |
| 3 | Analog Input 3 | R |
| 4 | Analog Input 4 | R |
| 5 | Analog Input 5 | R |
| 6 | Digital Output 0 | R/W |
| 7 | Digital Output 1 | R/W |
| 8 | Digital Output 2 | R/W |
| 9 | Digital Output 3 | R/W |
| 10 | Digital Output 4 | R/W |
| 11 | Digital Output 5 | R/W |
| 12 | Serial Interface Speed | R/W |
| 13 | Serial Interface Parity | R/W |
| 14 | Serial Interface Stop Bits | R/W |
| 15 | Serial Interface Timeout | R/W |
| 16 | Analog Input 0 NTC Temp | R |
| 17 | Analog Input 1 NTC Temp | R |
| 18 | Analog Input 2 NTC Temp | R |
| 19 | Analog Input 3 NTC Temp | R |
| 20 | Analog Input 4 NTC Temp | R |
| 21 | Analog Input 5 NTC Temp | R |

- Default Modbus TCP ID for accessing internal registers:	254

WEB interface

Use integrated web interface to monitor device and set parameters

Manual setting Digital Outputs

In “Digital Outputs” menu you can toggle the state of each digital output

Viewing analog inputs

You can view parameters of analog inputs in “Analog IO” menu

LAN Settings

LAN Settings can be changed in “LAN Settings” menu

Serial Interface Settings

Use “Serial Interface” menu to set parameters of the Serial Interface

- The changes take effect after reboot

Modbus Interface Status

The gateway shows Modbus Status in “Modbus Status” Menu

Restricting Modbus Access

Modbus TCP access can be restricted up to three IP addresses. To activate this function first request modbus data from the gateway and after that press “Unlocked” button